## HPT (hidden)
[5 empty] | VOLTAGE: | 480Y/277V | WIRE: |  | 4 |  | MOUNTING: | SURFACE |  | NOTES:
(E) PANEL 'HTP' |  |  |  |  | BUS RATING: | 225A | PHASE: |  | 3 |  | AIC RATING: | 14711
[5 empty] | MAIN REQUIREMENT: | 200A MLO | TYPE: |  | NEMA 1 |  | CONDITION: | EXISTING
CKT# | NOTES | LOAD | CB |  | LOAD DESCRIPTION |  | LOAD KVA | PHASE | LOAD KVA | LOAD DESCRIPTION |  |  | CB |  | LOAD | NOTES | CKT#
|  |  | P | T | [8 empty] | P | T
1 |  | ML | 3 | 60 | FC-1 |  | 15.789 | A | #REF! | 75kVA TRANSFORMER |  |  | 3 | 100 | D |  | 2
3 |  | ML |  |  |  |  | 15.789 | B | #REF! | [5 empty] | D |  | 4 | 56.1652
5 |  | ML |  |  |  |  | 15.789 | C | #REF! | [5 empty] | D |  | 6 | 47.367
7 |  | M | 3 | 40 | CU-1 |  | 2.6557 | A |  | EXIST |  |  | 1 | 20 | D |  | 8 | 0
9 |  | M |  |  |  |  | 2.6557 | B |  | EXIST |  |  | 1 | 20 | C |  | 10 | 0
11 |  | M |  |  |  |  | 2.6557 | C |  | SPARE |  |  | 1 | 20 |  |  | 12 | 1
13 |  |  | 1 | 20 | SPARE |  |  | A |  | SPARE |  |  | 1 | 20 |  |  | 14 | 1
15 |  |  | 1 | 20 | SPARE |  |  | B |  | SPARE |  |  | 1 | 20 |  |  | 16 | 1
17 |  |  | 1 | 20 | SPARE |  |  | C |  | SPARE |  |  | 1 | 20 |  |  | 18 | 0.65
19 |  |  | 1 | 20 | SPARE |  |  | A |  | SPARE |  |  | 1 | 20 |  |  | 20
21 |  |  | 1 | 20 | SPARE |  |  | B |  | SPARE |  |  | 1 | 20 |  |  | 22
23 |  |  | 1 | 20 | SPARE |  |  | C |  | SPARE |  |  | 1 | 20 |  |  | 24
25 |  |  |  |  | SPACE |  |  | A | 16.066 | RTU-1 |  |  | 3 | 60 | M |  | 26
27 |  |  |  |  | SPACE |  |  | B | 16.066 | [5 empty] | M |  | 28
29 |  |  |  |  | SPACE |  |  | C | 16.066 | [5 empty] | M |  | 30
31 |  |  |  |  | SPACE |  |  | A |  | SPACE | [6 empty] | 32
33 |  |  |  |  | SPACE |  |  | B |  | SPACE | [6 empty] | 34
35 |  |  |  |  | SPACE |  |  | C |  | SPACE | [6 empty] | 36
37 |  |  |  |  | SPACE |  |  | A |  | SPACE | [6 empty] | 38
39 |  |  |  |  | SPACE |  |  | B |  | SPACE | [6 empty] | 40
41 |  |  |  |  | SPACE |  |  | C |  | SPACE | [6 empty] | 42
CONNECTED LOAD: | [6 empty] | DEMAND LOAD CALCULATION
PHASE A |  |  |  |  | #REF! | KVA | DEMAND LOAD |  |  |  | SUBTOTAL | NEC DEMAND FACTOR
PHASE B |  |  |  |  | #REF! | KVA | CONTINUOUS LOAD (C) |  |  |  | 0 | 125% |  |  | 0
PHASE C |  |  |  |  | #REF! | KVA | DEDICATED LOAD (D) |  |  |  | #REF! | 100% |  |  | #REF!
TOTAL |  |  |  |  | #REF! | KVA | GENERAL RECEPTACLE (G) |  |  |  | 0 | 100% of 1st 10kVA & 50% of remaining |  |  | 0
[7 empty] | KITCHEN EQUIPMENT (K) |  |  |  | 0 | 65% |  |  | 0
[7 empty] | MOTOR LOAD (M)/(ML) |  |  |  | 103.5322 | 125% of largest motor load + 100% remaining |  |  | 115.3739
[12 empty] | TOTAL DEMAND KVA |  |  | #REF!
[12 empty] | AMPS @ 480Y/277V, 3 PHASE, 4WIRE: |  |  | #REF!

## A (2) (hidden)
[5 empty] | VOLTAGE: | 208Y/120V | WIRE: |  | 4 |  | MOUNTING: | SURFACE |  | NOTES:
(E)PANEL 'A' |  |  |  |  | BUS RATING: | 200A | PHASE: |  | 3 |  | AIC RATING: | 22000
[5 empty] | MAIN REQUIREMENT: | 200A MLO | TYPE: |  | NEMA 1 |  | CONDITION: | NEW
CKT# | NOTES | LOAD | CB |  | LOAD DESCRIPTION |  | LOAD KVA | PHASE | LOAD KVA | LOAD DESCRIPTION |  |  | CB |  | LOAD | NOTES | CKT#
|  |  | P | T | [8 empty] | P | T
1 |  | M | 1 | 20 | EF-1 |  | 0.2352 | A | 1.2 | SIGNAGE |  |  | 1 | 20 | C |  | 2
3 |  | M | 1 | 20 | EF-2 |  | 0.696 | B | 1.2 | SIGNAGE |  |  | 1 | 20 | C |  | 4 | 2.8224
5 |  | M | 1 | 20 | EF-3 |  | 0.2352 | C | 1.3562 | LTG - RECEPTION, WAITING, CORRIDOR |  |  | 1 | 20 | C |  | 6 | 0
7 |  | M | 1 | 20 | BF-1 |  | 1.656 | A | 0.8945 | LTG - RIGHT SIDE ROOMS |  |  | 1 | 20 | C |  | 8 | 0
9 |  | G | 1 | 20 | REC - ROOF |  | 0.36 | B | 0.94 | LTG - LEFT SIDE ROOMS |  |  | 1 | 20 | C |  | 10 | 0
11 |  | G | 1 | 20 | REC - URGENT #1, #2 - TV |  | 0.72 | C | 0.2 | WIRELESS HUB & TIMECLOCK |  |  | 1 | 20 | D |  | 12 | 1
13 |  | G | 1 | 20 | REC - SHOW WINDOW |  | 0.36 | A | 1.44 | REC - URGENT #1, #2 - CONVENIENCE |  |  | 1 | 20 | G |  | 14 | 1
15 |  | G | 1 | 20 | REC - LOBBY - TV + CONVENIENCE |  | 0.9 | B | 1.44 | REC - URGENT #3, #4 - CONVENIENCE |  |  | 1 | 20 | G |  | 16 | 1
17 |  | G | 1 | 20 | REC - LOBBY - CHECKIN TABLE |  | 0.54 | C | 1.44 | REC - PRIMARY #1, #2 - CONVENIENCE |  |  | 1 | 20 | G |  | 18 | 0.65
19 |  | G | 1 | 20 | REC - LOUNGE - TV + CONVENIENCE |  | 0.72 | A | 1.44 | REC - URGENT #1,#2,#3, #4 - GFI |  |  | 1 | 20 | G |  | 20
21 |  | G | 1 | 20 | REC - LOUNGE - FRIDGE |  | 0.5 | B | 0.54 | REC - CORRIDOR - CONVENIENCE |  |  | 1 | 20 | G |  | 22
23 |  | G | 1 | 20 | REC - LOUNGE - FOOD WASTE DISPOSER |  | 0.864 | C |  | SPARE |  |  | 1 | 20 |  |  | 24
25 |  | G | 1 | 20 | REC - LOUNGE - MICROWAVE |  | 1 | A | 1.44 | REC - PRIMARY #1,#2,#3, #4 - GFI |  |  | 1 | 20 | G |  | 26
27 |  | G | 1 | 20 | REC - LOUNGE - DISHWASHER |  | 1 | B | 0.72 | REC - URGENT #3, 4 - TV |  |  | 1 | 20 | G |  | 28
29 |  | G | 1 | 20 | REC - LOUNGE - MICROWAVE CABINET |  | 1 | C | 0.9 | REC - URGENT #3, #4, STAFF RR, PRIM #1, #3 - TL FAUCET |  |  | 1 | 20 | D |  | 30
31 |  | G | 1 | 20 | REC - LOUNGE - TOUCHLESS FAUCET |  | 1.44 | A | 0.9 | REC - PATIENT RR, PHLEB, HUB, URGENT #1, #2 - TL FAUCET |  |  | 1 | 20 | D |  | 32
33 |  | G | 1 | 20 | REC - LOUNGE - CONVENIENCE - GFI |  | 0.18 | B | 1.44 | REC - PRIMARY #3, #4 - CONVENIENCE |  |  | 1 | 20 | G |  | 34
35 |  | G | 1 | 20 | REC - PRIMARY #1, #2 - TV |  | 0.72 | C | 1.08 | REC - PRIMARY #3, #4 - GFI |  |  | 1 | 20 | G |  | 36
37 |  | G | 1 | 20 | RCP-1 |  | 0.18 | A | #REF! | PANEL 'B' |  |  | 3 | 100 | D |  | 38
39 |  | D | 2 | 60 | EWH-1 |  | 5 | B | #REF! | [5 empty] | D |  | 40
41 |  | D |  |  |  |  | 5 | C | #REF! | [5 empty] | D |  | 42
CONNECTED LOAD: | [6 empty] | DEMAND LOAD CALCULATION
PHASE A |  |  |  |  | #REF! | KVA | DEMAND LOAD |  |  |  | SUBTOTAL | NEC DEMAND FACTOR
PHASE B |  |  |  |  | #REF! | KVA | CONTINUOUS LOAD (C) |  |  |  | 5.5907 | 125% |  |  | 6.9884
PHASE C |  |  |  |  | #REF! | KVA | DEDICATED LOAD (D) |  |  |  | #REF! | 100% |  |  | #REF!
TOTAL |  |  |  |  | #REF! | KVA | GENERAL RECEPTACLE (G) |  |  |  | 21.464 | 100% of 1st 10kVA & 50% of remaining |  |  | 15.732
[7 empty] | KITCHEN EQUIPMENT (K) |  |  |  | 0 | 65% |  |  | 0
[7 empty] | MOTOR LOAD (M)/(ML) |  |  |  | 2.8224 | 125% of largest motor load + 100% remaining |  |  | 2.8224
[12 empty] | TOTAL DEMAND KVA |  |  | #REF!
[12 empty] | AMPS @ 208/120V, 3 PHASE, 4WIRE: |  |  | #REF!

## TEMPLATE
[5 empty] | VOLTAGE: | 120/208V | WIRE: |  | 4 |  | MOUNTING: | SURFACE |  | NOTES:
(E) PANEL "A" |  |  |  |  | BUS RATING: | 225A | PHASE: |  | 3 |  | AIC RATING: | EXISTING |  | FED FROM MAIN
[5 empty] | MAIN REQUIREMENT: | MLO | TYPE: |  | NEMA 1 |  | CONDITION: | EXISTING |  | SERVICE
CKT# | NOTES | LOAD | CB |  | LOAD DESCRIPTION |  | LOAD KVA | PHASE | LOAD KVA | LOAD DESCRIPTION |  |  | CB |  | LOAD | NOTES | CKT#
|  |  | P | T | [8 empty] | P | T
1 | [7 empty] | A | [8 empty] | 2
3 | [7 empty] | B | [8 empty] | 4
5 | [7 empty] | C | [8 empty] | 6
7 | [7 empty] | A | [8 empty] | 8
9 | [7 empty] | B | [8 empty] | 10
11 | [7 empty] | C | [8 empty] | 12
13 | [7 empty] | A | [8 empty] | 14
15 | [7 empty] | B | [8 empty] | 16
17 | [7 empty] | C | [8 empty] | 18
19 | [7 empty] | A | [8 empty] | 20
21 | [7 empty] | B | [8 empty] | 22
23 | [7 empty] | C | [8 empty] | 24
25 | [7 empty] | A | [8 empty] | 26
27 | [7 empty] | B | [8 empty] | 28
29 | [7 empty] | C | [8 empty] | 30
31 | [7 empty] | A | [8 empty] | 32
33 | [7 empty] | B | [8 empty] | 34
35 | [7 empty] | C | [8 empty] | 36
37 | [7 empty] | A | [8 empty] | 38
39 | [7 empty] | B | [8 empty] | 40
41 | [7 empty] | C | [8 empty] | 42
CONNECTED LOAD: | [6 empty] | DEMAND LOAD CALCULATION
PHASE A |  |  |  |  | 0 | KVA | DEMAND LOAD |  |  |  | SUBTOTAL | NEC DEMAND FACTOR
PHASE B |  |  |  |  | 0 | KVA | CONTINUOUS LOAD (C) |  |  |  | 0 | 125% |  |  | 0
PHASE C |  |  |  |  | 0 | KVA | DEDICATED LOAD (D) |  |  |  | 0 | 100% |  |  | 0
TOTAL |  |  |  |  | 0 | KVA | GENERAL RECEPTACLE (G) |  |  |  | 0 | 100% of 1st 10kVA & 50% of remaining |  |  | 0
[7 empty] | KITCHEN EQUIPMENT (K) |  |  |  | 0 | NEC Table 220.56 Demand Factor 100% |  |  | 0
NOTES | [6 empty] | MOTOR LOAD (M) |  |  |  | 0 | 100% of motor load |  |  | 0
1. EXISTING C/B WITH EXISTING LOAD. | [6 empty] | LARGEST MOTOR LOAD (ML) |  |  |  | 0 | 125% of largest motor load |  |  | 0
2. EXISTING C/B WITH NEW LOAD. | [6 empty] | NUMBER OF KITCHEN EQUIP. |  |  |  | 0 | TOTAL DEMAND KVA |  |  | 0
3. NEW C/B WITH NEW LOAD. | [11 empty] | AMPS @ 120/208V, 3 PHASE, 4 WIRE |  |  | 0
SUB PANEL 1
[7 empty] | DEMAND LOAD |  |  |  | SUBTOTAL
CONTINUOUS LOAD (C)
DEDICATED LOAD (D)
GENERAL RECEPTACLE (G)
KITCHEN EQUIPMENT (K)
MOTOR LOAD (M)
LARGEST MOTOR LOAD (ML)
NUMBER OF KITCHEN EQUIP.
SUB PANEL 2
[7 empty] | DEMAND LOAD |  |  |  | SUBTOTAL
CONTINUOUS LOAD (C)
DEDICATED LOAD (D)
GENERAL RECEPTACLE (G)
KITCHEN EQUIPMENT (K)
MOTOR LOAD (M)
LARGEST MOTOR LOAD (ML)
NUMBER OF KITCHEN EQUIP.
SUB PANEL 3
[7 empty] | DEMAND LOAD |  |  |  | SUBTOTAL
CONTINUOUS LOAD (C)
DEDICATED LOAD (D)
GENERAL RECEPTACLE (G)
KITCHEN EQUIPMENT (K)
MOTOR LOAD (M)
LARGEST MOTOR LOAD (ML)
NUMBER OF KITCHEN EQUIP.
STYLE TEXT
BORDERS

## _NOTES (hidden)
PANEL SCHEDULE NOTES
GENERAL NOTES:
CIRCUITS ITALICIZED ARE EXISTING TO REMAIN
BALANCE PANELS WITHIN 10% PHASE TO PHASE
PROVIDE UL LISTED HANDLE TIE FOR ALL MULTIWIRE BRANCH CIRCUITS
CIRCUIT KEYED NOTES:
LO | PROVIDE LOCK "ON" CLAMP DEVICE ON BREAKER
LF | PROVIDE LOCK "OFF" CLAMP DEVICE ON BREAKER
GFI | PROVIDE BREAKER WITH GROUND FAULT CIRCUIT INTERRUPT

## Ax (hidden)
[5 empty] | VOLTAGE: | 208Y/120V | WIRE: |  | 4 |  | MOUNTING: | SURFACE |  | NOTES:
PANEL 'A' (RL)PNL 'PC166' |  |  |  |  | BUS RATING: | 400A | PHASE: |  | 3 |  | AIC RATING: | 22000
[5 empty] | MAIN REQUIREMENT: | 400A MLO | TYPE: |  | NEMA 1 |  | CONDITION: | EXISTING
CKT# | NOTES | LOAD | CB |  | LOAD DESCRIPTION |  | LOAD KVA | PHASE | LOAD KVA | LOAD DESCRIPTION |  |  | CB |  | LOAD | NOTES | CKT#
|  |  | P | T | [8 empty] | P | T
1 |  | ML | 3 | 50 | RTU-1 |  | 4.68 | A | 1.2 | SIGNAGE |  |  | 1 | 20 | C |  | 2
3 |  | ML |  |  |  |  | 4.68 | B | 1.2 | SIGNAGE |  |  | 1 | 20 | C |  | 4 | 14.04
5 |  | ML |  |  |  |  | 4.68 | C | 0.858 | LTG - LOBBY, RR, PHLEBO, LAB, URGENT #1 - #2 |  |  | 1 | 20 | C |  | 6 | 14.04
7 |  | G | 1 | 20 | EF-1 |  | 0.528 | A | 0.89675 | LTG - URGENT #3 - #4, PRIM, RR, EVS, STO, LOUNGE, CONS |  |  | 1 | 20 | C |  | 8 | 0
9 |  | G | 1 | 20 | EF-2 |  | 0.36 | B | 0.822 | LTG - HUB, CORRIDORS |  |  | 1 | 20 | C |  | 10 | 0
11 |  | G | 1 | 20 | EF-3 |  | 0.36 | C | 0.36 | REC - SHOW WINDOW |  |  | 1 | 20 | C |  | 12 | 1
13 |  | G | 1 | 20 | REC - LOBBY - TV + CONVINIENCE |  | 0.72 | A | 1.44 | REC - URGENT #1, #2 - TV + BACKWALL |  |  | 1 | 20 | G |  | 14 | 1
15 |  |  |  |  | SPACE |  |  | B |  | SPACE | [6 empty] | 16 | 1
17 |  | G | 1 | 20 | REC - LOBBY - DESK + CONVINIENCE |  | 0.54 | C | 0.72 | REC - URGENT #3, PRIMARY - GFI |  |  | 1 | 20 | G |  | 18 | 0.65
19 |  |  |  |  | SPACE |  |  | A | 1.44 | REC - URGENT #3, PRIMARY - TV + BACKWALL |  |  | 1 | 20 | G |  | 20
21 |  |  |  |  | SPACE |  |  | B | 0.36 | REC - URGENT #4 - GFI |  |  | 1 | 20 | G |  | 22
23 |  |  |  |  | SPACE |  |  | C | 0.36 | REC - URGENT #1, #2 - CONVENIENCE |  |  | 1 | 20 | G |  | 24
25 |  | G | 1 | 20 | REC - LOBBY - CHECKIN TABLE |  | 0.54 | A | 0.72 | REC - URGENT #1, #2 - GFI |  |  | 1 | 20 | G |  | 26
27 |  |  |  |  | SPACE |  |  | B |  | SPACE | [6 empty] | 28
29 |  | G | 1 | 20 | REC - ROOF |  | 0.36 | C |  | SPACE | [6 empty] | 30
31 |  | M | 3 | 50 | RTU-2 |  | 4.68 | A | 0.72 | REC - URGENT #4 - TV + BACKWALL |  |  | 1 | 20 | G |  | 32
33 |  | M |  |  |  |  | 4.68 | B | 0.54 | REC - URGENT #3, #4, PRIMARY - CONVENIENCE |  |  | 1 | 20 | G |  | 34
35 |  | M |  |  |  |  | 4.68 | C |  | SPACE | [6 empty] | 36
37 |  | G | 1 | 20 | RCP-1 |  | 0.18 | A | #REF! | PANEL 'B' |  |  | 3 | 100 | D |  | 38
39 |  | D | 2 | 60 | EWH-1 |  | 5.625 | B | #REF! | [5 empty] | D |  | 40
41 |  | D |  |  |  |  | 5.625 | C | #REF! | [5 empty] | D |  | 42
CONNECTED LOAD: | [6 empty] | DEMAND LOAD CALCULATION
PHASE A |  |  |  |  | #REF! | KVA | DEMAND LOAD |  |  |  | SUBTOTAL | NEC DEMAND FACTOR
PHASE B |  |  |  |  | #REF! | KVA | CONTINUOUS LOAD (C) |  |  |  | 5.3368 | 125% |  |  | 6.6709
PHASE C |  |  |  |  | #REF! | KVA | DEDICATED LOAD (D) |  |  |  | #REF! | 100% |  |  | #REF!
TOTAL |  |  |  |  | #REF! | KVA | GENERAL RECEPTACLE (G) |  |  |  | 9.888 | 100% of 1st 10kVA & 50% of remaining |  |  | 9.888
[7 empty] | KITCHEN EQUIPMENT (K) |  |  |  | 0 | 65% |  |  | 0
[7 empty] | MOTOR LOAD (M)/(ML) |  |  |  | 28.08 | 125% of largest motor load + 100% remaining |  |  | 31.59
[12 empty] | TOTAL DEMAND KVA |  |  | #REF!
[12 empty] | AMPS @ 208/120V, 3 PHASE, 4WIRE: |  |  | #REF!

## Bx (hidden)
[5 empty] | VOLTAGE: | 208Y/120V | WIRE: |  | 4 |  | MOUNTING: | SURFACE |  | NOTES:
PANEL 'B' |  |  |  |  | BUS RATING: | 100A | PHASE: |  | 3 |  | AIC RATING: | 22000
[5 empty] | MAIN REQUIREMENT: | 100A MLO | TYPE: |  | NEMA 1 |  | CONDITION: | NEW
CKT# | NOTES | LOAD | CB |  | LOAD DESCRIPTION |  | LOAD KVA | PHASE | LOAD KVA | LOAD DESCRIPTION |  |  | CB |  | LOAD | NOTES | CKT#
|  |  | P | T | [8 empty] | P | T
1 |  |  | 1 | 20 | SPARE |  |  | A | 1 | REC - HUB - PRINTER |  |  | 1 | 20 | D |  | 2
3 |  | D | 1 | 20 | REC - PHLEBOTOMY - COUNTERTOP - GFI |  | 0.25 | B | 0.5 | REC - HUB - UC FRIDGE |  |  | 1 | 20 | G |  | 4 | 0
5 |  | G | 1 | 20 | REC - PHLEBOTOMY - CONVINIENCE |  | 0.25 | C | 0.25 | REC - HUB - COUNTERTOP - GFI |  |  | 1 | 20 | D |  | 6 | 0
7 |  | G | 1 | 20 | REC - LAB - UC FRIDGE |  | 0.5 | A | 0.72 | REC - HUB - TABLE |  |  | 1 | 20 | G |  | 8 | 0
9 |  | D | 1 | 20 | REC - LAB - COUNTER - GFI |  | 0.25 | B | 0.36 | REC - HUB - DESK |  |  | 1 | 20 | G |  | 10 | 0
11 |  | D | 1 | 20 | REC - LAB - COUNTER - GFI |  | 0.25 | C | 0.54 | REC - LOUNGE - TV + CONVINIENCE |  |  | 1 | 20 | G |  | 12 | 1
13 |  | G | 1 | 20 | REC - LAB - CONVINIENCE |  | 0.25 | A | 1 | REC - LOUNGE - REFRIGERATOR |  |  | 1 | 20 | G |  | 14 | 1
15 |  | G | 1 | 20 | REC - CONSULT - CONVINIENCE |  | 0.36 | B | 0.25 | REC - LOUNGE - COUNTERTOP - GFI |  |  | 1 | 20 | D |  | 16 | 1
17 |  | G | 1 | 20 | REC - STORAGE - CONVINIENCE |  | 0.36 | C | 0.864 | REC - LOUNGE - FOOD WASTE DISPOSER |  |  | 1 | 20 | D |  | 18 | 0.65
19 |  |  | 1 | 20 | SPARE |  |  | A |  | SPARE |  |  | 1 | 20 |  |  | 20
21 |  | G | 1 | 20 | REC - EVS - CONVINIENCE |  | 0.25 | B | 1 | REC - LOUNGE - DISHWASHER |  |  | 1 | 20 | D |  | 22
23 |  | G | 1 | 20 | REC - SCALE |  | 0.18 | C | 1.44 | REC - LOUNGE - TOUCLESS FAUCET |  |  | 1 | 20 | D |  | 24
25 |  | D | 1 | 20 | REC - STORAGE - IT RACK |  | 0.5 | A | 0.72 | REC - URGENT #1, #2, #3, #4 - TOUCLESS FAUCET |  |  | 1 | 20 | D |  | 26
27 |  | D | 1 | 20 | REC - STORAGE - TELEBOARD |  | 0.5 | B | 0.72 | REC - RESTRMS, HUB, PRIMARY - TOUCLESS FAUCET |  |  | 1 | 20 | D |  | 28
29 |  | D | 1 | 20 | REC - STORAGE - TELEBOARD |  | 0.5 | C |  | SPARE |  |  | 1 | 20 |  |  | 30
31 | [7 empty] | A | [8 empty] | 32
33 | [7 empty] | B | [8 empty] | 34
35 | [7 empty] | C | [8 empty] | 36
37 | [7 empty] | A | [8 empty] | 38
39 | [7 empty] | B | [8 empty] | 40
41 | [7 empty] | C | [8 empty] | 42
CONNECTED LOAD: | [6 empty] | DEMAND LOAD CALCULATION
PHASE A |  |  |  |  | 4.69 | KVA | DEMAND LOAD |  |  |  | SUBTOTAL | NEC DEMAND FACTOR
PHASE B |  |  |  |  | 4.44 | KVA | CONTINUOUS LOAD (C) |  |  |  | 0 | 125% |  |  | 0
PHASE C |  |  |  |  | 4.634 | KVA | DEDICATED LOAD (D) |  |  |  | 8.494 | 100% |  |  | 8.494
TOTAL |  |  |  |  | 13.764 | KVA | GENERAL RECEPTACLE (G) |  |  |  | 5.27 | 100% of 1st 10kVA & 50% of remaining |  |  | 5.27
[7 empty] | KITCHEN EQUIPMENT (K) |  |  |  | 0 | 65% |  |  | 0
[7 empty] | MOTOR LOAD (M)/(ML) |  |  |  | 0 | 125% of largest motor load + 100% remaining |  |  | 0
[12 empty] | TOTAL DEMAND KVA |  |  | 13.764
[12 empty] | AMPS @ 208/120V, 3 PHASE, 4WIRE: |  |  | 38.2333

## L109C_NOTUSED (hidden)
[5 empty] | VOLTAGE: | 208Y/120V | WIRE: |  | 3 |  | MOUNTING: | RECESSED |  | NOTES:
PANEL 'L109C' |  |  |  |  | BUS RATING: | 100A | PHASE: |  | 1 |  | AIC RATING: | 10000
[5 empty] | MAIN REQUIREMENT: | 100A MLO | TYPE: |  |  |  | CONDITION: | NEW
CKT# | NOTES | LOAD | CB |  | LOAD DESCRIPTION |  | LOAD KVA | PHASE | LOAD KVA |  | LOAD DESCRIPTION |  | CB |  | LOAD | NOTES | CKT#
|  |  | P | T | [8 empty] | P | T
1 |  | G | 1 | 20 | REC - X-RAY ROOM TABLE |  | 0.36 | A |  | SPARE |  |  | 1 | 20 |  |  | 2
3 |  | G | 1 | 20 | REC - X-RAY ROOM CONVENIENCE |  | 0.36 | B |  | SPARE |  |  | 1 | 20 |  |  | 4 | 0
5 |  | D | 1 | 20 | REC - X-RAY ROOM PORTABLE X-RAY |  | 1 | A |  | SPARE |  |  | 1 | 20 |  |  | 6 | 0
7 |  |  |  |  | SPACE |  |  | B |  | SPACE | [6 empty] | 8 | 0
9 |  |  |  |  | SPACE |  |  | A | 0.104 | FIXED X-RAY |  |  | 2 | 150 | D |  | 10 | 0
11 |  |  |  |  | SPACE |  |  | B | 0.104 | ----- |  |  | - | - | D |  | 12 | 1
13 |  |  | 1 | 20 |  |  |  | A |  |  |  |  | 1 | 20 |  |  | 14 | 1
15 |  |  | 1 | 20 |  |  |  | B |  |  |  |  | 1 | 20 |  |  | 16 | 1
17 |  |  | 1 | 20 |  |  |  | C |  |  |  |  | 1 | 20 |  |  | 18 | 0.65
19 |  |  | 1 | 20 |  |  |  | A |  |  |  |  | 1 | 20 |  |  | 20
21 |  |  | 1 | 20 |  |  |  | B |  |  |  |  | 1 | 20 |  |  | 22
23 |  |  | 1 | 20 |  |  |  | C |  |  |  |  | 1 | 20 |  |  | 24
25 |  |  | 1 | 20 |  |  |  | A |  |  |  |  | 1 | 20 |  |  | 26
27 |  |  | 1 | 20 |  |  |  | B |  |  |  |  | 1 | 20 |  |  | 28
29 |  |  | 1 | 20 |  |  |  | C |  |  |  |  | 1 | 20 |  |  | 30
31 |  |  | 1 | 20 |  |  |  | A | [8 empty] | 32
33 |  |  | 1 | 20 |  |  |  | B | [8 empty] | 34
35 |  |  | 1 | 20 |  |  |  | C | [8 empty] | 36
37 |  |  | 1 | 20 |  |  |  | A | [8 empty] | 38
39 |  |  | 1 | 20 |  |  |  | B | [8 empty] | 40
41 |  |  | 1 | 20 |  |  |  | C | [8 empty] | 42
CONNECTED LOAD: | [11 empty] | DEMAND LOAD CALCULATION
PHASE A |  |  |  |  | 1.464 | KVA | DEMAND LOAD |  |  |  | SUBTOTAL | NEC DEMAND FACTOR
PHASE B |  |  |  |  | 0.464 | KVA | CONTINUOUS LOAD (C) |  |  |  | 0 | 125% |  |  |  | 0
[7 empty] | DEDICATED LOAD (D) |  |  |  | 1.208 | 100% |  |  |  | 1.208
TOTAL |  |  |  |  | 1.928 | KVA | GENERAL RECEPTACLE (G) |  |  |  | 0.72 | 100% of 1st 10kVA & 50% of remaining |  |  |  | 0.72
[7 empty] | KITCHEN EQUIPMENT (K) |  |  |  | 0 | 65% |  |  |  | 0
[7 empty] | MOTOR LOAD (M)/(ML) |  |  |  | 0 | 125% of largest motor load + 100% remaining |  |  |  | 0
[12 empty] | TOTAL DEMAND KVA |  |  |  | 1.928
[12 empty] | AMPS @ 208/120V, 1 PHASE, 3WIRE: |  |  |  | 9.2692